Electrical Requirements for New Work

And Construction

I.  Contractors expectations:

- All new electrical work shall be performed by a qualified electrical contractor that is 	licensed and bonded applying NFPA 70-2020, NFPA 99-2012 and NFPA 70e 2015 or the most current applicable standard for the authority having jurisdiction for all electrical work performed for UMC with the exception of the following articles which must be complied with as listed unless otherwise approved by Hospital Management in writing. In the event there is conflict between any code requirement and the exceptions of this list, the most stringent rule shall apply.

  - Anyone that works at UMC will need to sign in and out at engineering office, wear a hospital badge at all times at work and must receive Contractor’s Orientation at least once which is performed every Thursday at 8:30am. Arrangements shall be made within at least 24 hours of anticipation to schedule a required one time 45 minutes safety orientation. The training shall be scheduled with Mindy Aparicio of the Engineering Department main office at 521-7640.

  - All electrical contractor personnel must arrive in presentable attire.  No ripped shirts or ripped pants etc… It is recommended for personnel to wear a uniform with company logo. When working on Hospital public areas the contractor must abide to Hospital Appearance Policies.

  - Regardless of which department contracted your Electrical Service Company, all contractors must notify any one of UMC electrical staff upon arrival and upon completion of work to inspect for proper installation.  UMC electrical staff will acknowledge the intended scope of work, assess its feasibility and safe execution and to conduct a mandatory NFPA 70e 2015 article 110.1 (a,b,c)  Pre Job briefing meeting which must be signed by all members participating in the execution of the job scope intended for each working day. The Electrical contractor must make all necessary provisions to participate and fully comply with this mandatory requirement.

  - A load assessment shall be performed by the contactor anytime his proposal includes connecting to an existing circuit. Amperage and voltage readings must be performed prior to the installation to avoid overload.  The information taken must be made available to UMC electricians for evaluation.  The scope of work when connecting to existing circuits must be preapproved in writing ( Email or signed shop drawings etc.) by a member of UMC electrical service team after making available

- When working in the ceiling, “Above the Ceiling Permits” must be filled out prior to starting work & must have a copy with them on job site at ALL times. Contractor to have the project PO# written on the permit in order to have permit approved.

  - The Contractor must ensure that all boxes are covered, all knockouts are sealed.

  - Any unacceptable job conditions found at the time of the work execution and that are not part of the scope of work ( open boxes, fire penetrations, exposed wires, unsafe conditions etc.) shall be documented and brought back to the attention of the UMC Electrician overseeing the job related with the scope of work. Any items not reported an opportune time might be considered the responsibility of the contractor to correct or repair.

II. Electrical requirements for new installations.

- Any time a contractor performs any work on a distribution panel, switchboard, motor control center that will change the designation / accuracy of any element on the panel schedule or the accuracy of the existing labels on any equipment, the contractor is responsible to furnish and install new labels / panel schedules in conformity to NEC 70, 70e and this UMC electrical requirements for new constriction whichever is stricter. Any changes made to a panel schedules must be typed and Not hand written.

    - Electrical equipment to be identified with nameplates includes: Distribution panels, Lighting panelboards, switchboards, transformers, disconnects, and all other electrical equipment.

    - Nameplates shall be required to be color coded in accordance with the color code stated in the table below. Provide appropriately color coded plastic laminated nameplates at all locations of major units of the electrical equipment as stated above. Nameplates shall be constructed from laminated phenolic plastic, 1/8 inch thick, 3-ply colored surfaces with white core. Engraving shall be with Roman Gothic lettering, 3/16 inch high, appropriately spaced. The Nameplate shall be attached to the control devices by use of self tapping flat head chromium plated screws  unless approved otherwise.

    - The nameplate must include where the equipment it fed from.

2.  All conduit and wiring shall be installed in a neat and presentable manner.

A. All box covers, receptacles, and switches shall be permanently identified 	            	        with the panel name and the circuit number.

B.  All homeruns that shall be ¾” conduit or larger.

C.  EMT fittings must be rain tight for outdoors and compression type for indoors.

D.  Boxes must be at least 2 ½” Deep unless approved by UMC.

E.  At least 10” of free conductor, measured from the point in the box where it 			  emerges from the raceway.

F.  Homeruns shall be at least number 10 AWG and must be THHN or 			                   equivalent.

Exception: In an Ungrounded Isolated Power System conductors must be         	at least number 10 AWG stranded with XHHW insulation or equivalent.

Conductors must be brown and orange in color.  The brown conductor 			must be terminated on the brass screw on the receptacle and the orange 			conductor on the silver screw.

- On a 120 – 208 Volt wye system black, red, blue, and white conductors 		must be used and on a 277-480 Volt wye system brown, orange, yellow, 		and gray must be used.

- Branch circuits that have a different voltage shall not be installed in the          	same raceway or box.

- Similarly, branch circuits from different branches of the emergency & normal power systems shall not be installed in the same raceway or box.

- If running outside (roofs. floor, etc.) conduit shall be rigid.

- If running on roof DURA BLOCKS to be used for strapping and NOT wood blocks.

- In accordance with NEC Article 517.13(A) Wiring Methods, all branch circuits installed in a patient care area shall be installed in a metal raceway.

- If less than or equal to 100 amps or wire sizes 12 to 1 AWG conductors, the contractor must size all conductors based on the 60 degrees Celsius wire ampacity selection column.

- If greater than 100 amps or larger than 1 AWG conductor, the contractor must size conductors based on the 75 degree Celsius wire ampacity selection column.

- Regardless of the wire selection method used as permitted by bullets M or N on this document, all equipment installations, termination, wire size, wire splices shall be made to comply with the 90 degree Celsius wire ampacity column.

- The contractor is responsible to provide installations to comply with the voltage drop requirements stated in the 2014 NFPA NEC 70 code Article 210.19 (a) fpn 4. UMC will verify compliance with this article at full load and the contractor is solely responsible to correct at their own cost any installation performed that does not meet the requirement under the referred article.

- Device requirements.

A.  All receptacles shall be hospital grade, rated 20amps, and installed with the 	           ground prong on top.

B.  Switches shall be spec grade.

C.  All Multi-Strips outlets must be UL hospital approved and hospital grade type outlet.  Shall be secured and fixed to the wall or equipment served.

3.   Lighting

A.  Color temperature on fluorescent lamps must be 4100 Kelvins or 5,000 Kelvins when specified by UMC staff.

B.  Outside lighting shall comply with the City Light Ordinance.

C.  All lay in light fixtures to be supported by their own independent distinct colored   wire.  No less than two independent points of attachment and the wire shall be independently secured to the deck or roof structure (joists).

D.  All light switch locations shall be provided with a grounded conductor at all new installation work. The application of provisions as stated on Article 404.2( c ) exceptions shall be requested for UMC approval in writing at the time of submitting the quote or at any time during the job execution. UMC will decide on the acceptance of the request for exceptions for each job proposal.

E. For new construction all recess can type lighting must be L.E.D and completely sealed recessed light cover assembly without a perforation opening above ceiling plenum. Regardless if plans or project show otherwise. It is the responsibility of the contractor to obtain authorization in writing from the UMC Electrical team or Manager, Director before deviating from this requirement. LED down lights must be Envision LED-SL-PNL-8R-22W-5CCT-0/10V or approved equivalent approved by UMC Engineering Electricians

F. Any new exit sign or emergency “Frog Eye” fixtures or indoor egress lights must be smart self-testing Hexmodal type. White border with red letters. Hexmodal | Every CMS Test - Automated unless otherwise approved.

4.   Panel boards will be “bolt on” type Square D or approved equal. Different termination (Snap on) shall not be used unless otherwise approved by Hospital.

5.   All standard covers must be stainless steel.

6.   No more than 6’ of FMC, HCF90 Cable, etc. unless approved by Hospital Electrician or   supervisors.

7.  No PVC raceways shall be allowed in hospital.

8. Under no circumstance a breaker is to be turned Off before getting approval from Hospital Electricians or Supervisors. Two levels of overcurrent protection from the load must be investigated before working with a circuit hot.

9. Under no circumstance is a job site with tools, materials, or open ceiling tiles to be left unattended.   All items are to be on a moveable cart, ladders removed and ceiling tiles put back before leaving a work area with no restricted access.

10.  Never leave any live, open, or etc. for any reason without Supervision.

11.  No Quads on patient care areas (TDH)

12.  No flex or raceway should be approved for grounding path ( A equipment grounding conductor shall be run through the raceway at all times).

13.  Tamper Proof outlets will be required to be used in any Pedi area’s, waiting rooms, ER, etc. (any place kids may be present) 20 amp Hospital Grade Receptacle tamper proof.

14.  Fire Alarm:  any work will need to go through electrician or management & correct paper work to be filled out.

15.  Rigid conduit to be used on runs outside below 6ft or tops.

16. Contractor must have at least one licensed Texas Journeyman Electrician on site while performing electrical work at UMC premises and contractor must be ready to provide copies of Journeyman & Master Electrician license upon request.

17.  Contractors need to contact UMC Electricians when they are present to perform any work in UMC.

18.  There must be a qualified person such as a Journeyman Electrician present at all times

19.  All work on electrical equipment must be performed de-energized. Proper documentation and coordination must be followed to minimize the impact to the Hospital.

20.  In the event electrical work needs to be performed while energized, an energized work permit must be filled out with the approval and signatures of the Safety Department

21.  Conductors shall be color coded by the Voltage a per table below;

| Voltage | Phase A | Phase B | Phase C | Neutral | Ground |
| --- | --- | --- | --- | --- | --- |
| 480V | Brown | Orange | Yellow | Gray | Green |
| 208V | Black | Red | Blue | White | Green |

22. Color Coding for Hospital Electrical Branches shall be as follows:

| Branch | Color |
| --- | --- |
| Normal | Black |
| Critical | Orange |
| Life Safety | Yellow |
| Equipment | Blue |
| Fire Alarm | Red |
| Low Voltage Control wiring | Pink |
| Emergency Power Before ATS | Red |

23.  When MC cable is being used, the contractor shall install the cable shall be identified according to the voltage it is feeding such as 120v a black band around the metal jacket of an MC cable and for 277v a cable with a brown band shall be used.

24.  When adding circuits to an electrical panel the Contractor must revise the panel schedule.

25.  The Electrical panel shall not have a spare breaker with an existing conductor on it. In the event this condition exists, it must be bought to the attention of the UMC Electricians immediately.

26.  To prevent an unintended ground fault condition and to minimize risk of an electrical shock, all metal parts of the electrical system that is likely to become energized, must be bonded to the building grounding system.

27.  Any unsafe condition that is observed must be brought to the attention of the Electricians or management immediately.

28.  As per NFPA 25 5.2.2.2 – “Sprinkler piping shall not be subjected to external loads by materials either resting on the pipe or hung from the pipe.”

29.  All firewall penetrations shall be sealed with SSS firestop products and the installer must be a certified for SSS products. Please get in contact with Grainger Supply for certification information

30. Impact guns will not be allowed to be used to open and close electrical panels.

31. Contractor to supply their own PPE, Bunny Suits and Zip Walls.

32. Any new transformers will be minimum 75KVA K-Type 5X in Rush.

33. Temporary Emergency Standby Generator Power

- Every time that UMC requires or request contract service to provide a temporary emergency generator the following shall apply unless otherwise approved by the UMC project manager requesting the service and must be in writing.

- The temporary emergency generator must be of equal or greater capacity as existing building emergency generator.

- Contractor will need to provide generator with a full tank of diesel.

- The generator must be Emergency Power Grade to meet NFPA 110 requirements for Hospital Service NFPA 99 category 1 NFPA 110 Level 1

- The generator must be in good operational order. (UMC might ask at any time for the records of service if deemed necessary).

- In order to prevent that a generator with hidden failure conditions is set up in place causing danger to the intended operation, UMC requires to load bank temporary portable generator to at least 80% of full rated capacity and provide the proper documentation that load test passed before connecting to building load.

- If the scope of work is a turnkey project then the contractor is also responsible to provide the appropriate cabling, connectors, extension cords, Polaris lugs, etc. needed to tie in portable generator to building load

    - Contractor is also responsible to tie in ATS start signal and verify ATS’s are working correctly with temporary generator.

    - Contractor is also responsible to connect any associated generator equipment such as coolant heater, battery charger, etc. that is on the temporary portable generator.

    - Contractor is also responsible to disconnect all temporary wiring and reconnect existing building ATS start signal and verify proper function of building generator and associated ATS’s before removing temporary portable generator from UMC site.

34.  Low Voltage wiring 50 volts or less will be spliced with UMC approved WAGO connectors or with UMC approved butt splices.

I , ____________________________ representing the Electrical Service Company

designated as ______________________________________ acknowledge that I received,

read and will comply with the specific requirements of this document while working for

UMC on any Electrical Work.                                    Date; ________________________

Signature;________________________

________________________________

Revised by; Pedro Baca, Jonathan Cortez, Steve Ferguson

Roberto Valadez Director of Engineering